SUNY DOWNSTATE MEDICAL CENTER

UNIVERSITY HOSPITAL OF BROOKLYN

POLICY AND PROCEDURE

No:  Section 17B

Page 1 of 4

Subject:  Guidelines for Infection Control

Facilities, Management and Development		Original Issue date:  1982

Prepared by:  George Allen, Ph.D., CIC		Supercedes:		June 2003

Reviewed/Approved by:				Approval Date:	April 2007

Michael Augenbraun, MD, FACP

Distribution:	Infection Control Manual

Issued by:  Infection Control Program

___________________________________________________________________________

I.	Purpose: To provide guidelines for the prevention of the transmission of communicable

diseases and other infections from the environment and equipment utilized at this facility.

II.	Definition: None

III.	Policy: A clean and safe environment will be maintained through constant inspection, 	preventative maintenance and timely repair of equipment.

IV.	Role Responsibility: Department head/designee, director of physical plant or administrator 	will ensure compliance.

V.	Procedure/Guidelines:

Patient Environment

All surfaces - floors, walls, and ceilings require constant inspection and timely repair when

necessary, in order to maintain smooth, dry, cleanable surfaces. Any openings or breaks in the

walls, foundation, window frames, etc. require timely repair in order to preserve a clean

environment.

Rodent and Pest Control

Rodent control is accomplished by the use of rodenticide which must be administered by a

licensed exterminator and is predominantly contractual work.  Treat non patient areas routinely

with an efficacious residual insecticides.  Insecticides must be administered by a licensed

exterminator. Extermination is predominantly outside contract work administered by

environmental services. In patient rooms, the hospital exterminating service will use insecticides

for a definite and specific problem only, selecting the lowest possible level of toxicity (see

Housekeeping guidelines).

The ultra-violet bulb in the insect electrocuter should be checked by Facilities, Management and

Development (FM&D) on a regular basis, and for a maximum effectiveness the bulbs should be

Changed when necessary.

On a daily basis the following should be performed:	A thorough hosing of the entire yard and

loading area including the area around and under the compactor by building services. All debris

that is not washed down the drain shall be swept up for disposal. Each entrance from the yard

shall be checked daily to ensure that the doors and air screens work properly. All doors and

entrances shall be kept closed and ensured  so by the designated department utilizing that

entrance.

Hospital Environmental Considerations

Disposal of blood and other body fluids is through the sewer system. Trash, if properly bagged,

can be transferred by chutes to the compactor. Waste from the clinical labs, surgical pathology

and designated special area is to be treated as regulated medical waste.

Putrescible wastes, if collected by a collection service, shall be retained in watertight

receptacles of impervious material in tight-fitting closures (e.g., dumpsters) that will protect the

contents from flies, insects, rats, and other animals. A thorough clearing and disinfecting of the

area under and around the compactors is performed on a daily basis.

Construction Dust Control

Prior to the start of a project, all items used for the care of patients must be removed from the

immediate area. Dust in the construction area shall be contained by the use of a full height dust

tight non-combustible partition or whenever possible by a closed door.  If either measure is

ineffective, an alternate barrier, including creating a negative pressure gradient, must be

identified before work may resume. Dust mats placed directly outside of the work area must be

maintained in a sanitary manner and all construction waste must be transported covered when

passing adjacent to patient care areas. The hospital housekeeping department shall be notified

at the start and completion of all construction work and will be available as consultants for

maintaining a sanitary environment.

Personnel

Personnel shall comply with pre-employment and annual health exam requirements and

procedures as outlined in the ICM, Section 20. Protective outer clothing and safety apparatus

shall be worn when maintenance personnel are exposed to contaminated waste (dumpsters,

broken sewage lines, and any other contaminated fluid which is likely to soil their clothing).

Maintenance personnel shall follow the dress code for specific areas (Isolation Precaution

Rooms, OR, etc.).

Personnel shall comply with the hospital’s policies regarding attending annual infection control

in service program.  Attendance shall be documented. Universal/Standard Precaution must be

used. Hands must be washed after contact with any body substance.

Hospital Cooling Tower

To avoid cooling tower contamination with Legionella, the following must be assured:

A thorough cleaning of all condensate, scrub down and disinfection of the tower shall be

performed at the start and end of the air conditioning season. An additional chlorine disinfection

process shall be performed in mid August.

A Bromicide solution shall be continuously fed to the tower by means of an automatic feeder,

the level of 0.2 to 0.5ppm shall be maintained.  The PH shall be maintained between 7.5 and

9.0 with 9.2 being optimum.  A maintenance log shall be kept. Documentation of chemical

treatments shall be maintained.

Fan Coil Units

Filters in patient care areas shall be changed and dated. The entire unit shall be vacuumed

when the filter is changed. An investigation of the unit for standing (un-drained) water and

subsequent correction must be undertaken and documented.

Air Filters on Air Handling Units

All unit filters are cleaned or replaced when the resistance to air flow has increased to two times

the original resistance, or when the manufacturer recommends it. The neonatal unit air

conditioning system filter is replaced every 3 months as a minimum standard.

Disposable filters are never cleaned and reused. Filters used for high risk areas (ORs, ICU,

Bone Marrow, CCU, etc) may be comprised of two types.  Zone Filters, changed quarterly; Roll

Filters are adjusted weekly and changed approximately five times a year. HEPA filters are

changed in accordance to manufacturers’ recommendations.

Ventilation Systems of the OR and L&D shall incorporate air filters with an efficiency of not less

than 90%.  A humidity of 50% to 60% must be maintained to control airborne bacteria in OR and

delivery room.  The room temperature in OR and delivery rooms shall be maintained between

70o and 76oF unless designated and approved.  In order to ensure appropriate air quality, FM&D

will periodically assess air changes in the ICU, OR and L&D areas.

Equipment

The hospital water supply system shall not be connected with other non potable piping systems

or with fixtures that could allow contamination.  Water supplies are protected from contamination

by the installation of vacuum breakers, check valves, back-flow-preventors, RPZs and subjected

to routine inspections.

Drains are never installed in the operating or delivery rooms. Aerators are not routinely installed

on faucets.  Aerators can provide a rich medium for the growth of Pseudomonas and Legionella

species.  Therefore, if an aerator is installed, infection control should be notified and a program

developed and implemented for regular inspection and cleaning of these aerators.

Water fountains are inspected as necessary. Filters are replaced following an established

schedule.

Supply and exhaust air openings are located at least three inches above the floor when located

less that seven feet above the floor, inlet and outlet openings shall be protected by a grill or

screen with openings not larger than A” mesh.

All fans serving exhaust vents shall be located at the discharge end of the system. All air

supplied to the OR shall be delivered at or near the ceiling; all air exhausted is removed near

floor level.  At least two exhaust outlet shall be used in all ORs and Delivery rooms.  OR air is

supplied from the outside through filters and then is exhausted directly outdoors.  The exhaust

outlet must be separated from the intake port.

Piped-in Gases

Oxygen, nitrous oxide and other medical gas systems are installed and operated in compliance

with the National Fire Protection Association.  Filter mechanisms must be used/maintained to

decrease the incidence of contamination.

CONTROLS ON THE SYSTEM

Written routine procedures and schedules for the evaluation of the quality of the ventilation

system, water supplies, and piped-in gases shall be formulated according to manufacturers’

recommendations and acceptable standards by agencies having jurisdictional control. The

Hospital Epidemiologist/designee may order and review environmental cultures, as necessary.

PREVENTIVE MAINTENANCE OF PORTABLE HEPA FILTER MACHINES

The HEPA pre-filter should be replaced once every other month on a regular basis.  However, if

at any time after visual inspection the filter is dirty and replacement is required, notification to

FM&D will be made by Central Sterile staff to have the filter changed.

A filter Preventive Maintenance (PM) Program will be in effect on all HEPA filter units. After

initial replacement, a sticker is affixed to the HEPA filter indicating a PM due date.  After each

patient use of a filter, the unit is cleaned and the PM sticker is checked.  If the unit is due for

PM, contact is made to the Control Room for maintenance.

After the filter is replaced, a new PM sticker is applied with a two month duration date.  The unit

is then covered and put back in service. The internal HEPA filter will be changed following a

schedule established by FM&D.

TB Isolation Room Testing/Monitoring

Isolation rooms maybe monitored when in use continuously by electronic instruments and a

distinct alarm alerts staff if negative pressurization falls below setting.  The Control Room must

be notified if this occurs.

Negative pressure, directional air flow and ventilation for dilution and exhaust test using a

smoke stick must be conducted and documented on a daily basis.

VI:	Reason for Revision: Review

VII:	Attachments:  None

VIII:	References: CDC, APIC

| Date Reviewed | Revision Required (Check One) |  | Responsible Staff Name and Title |
| --- | --- | --- | --- |
| 4/07 | Yes |  | George Allen, Ph.D. Dir. of Infection Control |
|  | Yes | Yes |  |
|  | Yes | Yes |  |
|  | Yes | Yes |  |